## Sheet1
Item of Requisition |  | Item 10 | Item 30 | Item 120 | Item 170 | Item 230 | Item 240 | Item 370 | Item 420 | Item 430 | Item 440 | Item 450 | Item 460 | Item 470 | Item 500 | Item 570
| Material Code | 6603020393 | 6603020883 | 6603430379 | 6603430237 | 6603060075 | 6603430009 | 6609901713 | 6603210598 | 6603062003 | 6603430186 | 6603430187 | 6603430189 | 6603430198 | 6603360893 | 6603430850
| Quantity Required | 1 | 2 | 1 | 1 | 3 | 1 | 4 | 1 | 2 | 2 | 10 | 2 | 2 | 1 | 1
MOTOR NAME PLATE PICTURE
Application |  | HOIST UP/DOWN MOTOR | PADDLE FEEDER TRAVEL MOTOR | HP/LP BYPASS RECIRCULATION | Mill Lube oil motor | UAT/ST Transformer Cooling Fans | GT Cooling Fans | ROOF EXHAUST FAN | ERH VIBRO FEEDER | Package AC outdoor fan motor | Package AC outdoor fan motor | Package AC outdoor fan motor | Package AC outdoor fan motor | Package AC outdoor fan motor | HP/LP Bypass Blower Motor | Instrument Air Compressor Dryer Motor
H.Area |  | SAFE | SAFE | SAFE | SAFE | SAFE | SAFE | SAFE | SAFE | SAFE | SAFE | SAFE | SAFE | SAFE | SAFE | SAFE
Type |  | SQUIRREL CAGE INDUCTION MOTOR | SQUIRREL CAGE INDUCTION MOTOR | SQUIRREL CAGE INDUCTION MOTOR | SQUIRREL CAGE INDUCTION MOTOR | SQUIRREL CAGE INDUCTION MOTOR | SQUIRREL CAGE INDUCTION MOTOR | SQUIRREL CAGE INDUCTION MOTOR | SQUIRREL CAGE INDUCTION MOTOR | SQUIRREL CAGE INDUCTION MOTOR | SQUIRREL CAGE INDUCTION MOTOR | SQUIRREL CAGE INDUCTION MOTOR | SQUIRREL CAGE INDUCTION MOTOR | SQUIRREL CAGE INDUCTION MOTOR | SQUIRREL CAGE INDUCTION MOTOR | SQUIRREL CAGE INDUCTION MOTOR
Mounting |  | B5 | B5 | V1 | V1 | B3 | B3 | B3 | B3 | B3 | B3 | B3 | B3 | B3 | B14 | Flange Mounted(B5)
Frame |  | 100 | 100L | TYPE:,YSJ6314-3 | YD160L-8/4 | BVM61063 | Type:DBE-5Q6TH | MODEL No.- DH-105 | FU680-6.4.1 | Model No. - YDK120-8N | Model No. - LK4110 | Model No: LK4111 | Model No. - LK4109 | Type - 2HS1 090-0503-A00002 | FT85 | Type - MM56 4-0MLT
Output (kW) |  | 3.7 | 0.75/1.1(DUAL SPEED) | 0.12 | 7/11(DUAL SPEED) | 0.5 | 0.37 | 5.5 | 2.7 | 120 Watt | 370 Watt | 250 Watt | 750 Watt | 370 Watt | 0.25 | 0.02/0.03
Voltage (V) |  | 415V+/-10% | 415V+/-10% | 415V+/-10% | 415V+/-10% | 415V+/-10% | 415V+/-10% | 415V+/-10% | 415V+/-10% | 230V+/-10% | 230V+/-10% | 230V+/-10% | 230V+/-10% | 230V+/-10% | 415V+/-10% | 230V+/-10%
Frequency(Hz) |  | 50HZ+/-5% | 50HZ+/-5% | 50HZ+/-5% | 50HZ+/-5% | 50HZ+/-5% | 50HZ+/-5% | 50HZ+/-5% | 50HZ+/-5% | 50HZ+/-5% | 50HZ+/-5% | 50HZ+/-5% | 50HZ+/-5% | 50HZ+/-5% | 50HZ+/-5% | 50HZ+/-5%
Method of starting |  | DOL | DOL | DOL | DOL | DOL | DOL | DOL | DOL | DOL | DOL | DOL | DOL | DOL | DOL | DOL
Cooling |  | IC411 | IC411 | IC411 | IC411 | IC411 | IC411 | IC411 | IC411 | IC411 | IC411 | IC411 | IC411 | IC411 | IC411 | IC411
Protection |  | IP55 | IP55 | IP55 | IP55 | IP55 | IP55 | IP55 | IP55 | IP55 | IP55 | IP55 | IP55 | IP55 | IP55 | IP55
EFF class |  | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2 | IE2
Ambt temp |  | 50⁰ C | 50⁰ C | 50⁰ C | 50⁰ C | 50⁰ C | 50⁰ C | 50⁰ C | 50⁰ C | 50⁰ C | 50⁰ C | 50⁰ C | 50⁰ C | 50⁰ C | 50⁰ C | 50⁰ C
Full Load Speed(rpm) |  | 1420 | 740/1400 | 1400 | 730/1450 | 900 | 960 | 960 | 980 | 750 | 920 | 920 | 920 | 940 | 1359 | 1450/1705
Full Load Current (Amp) |  | 7.8 | 2.33 | 0.43 | 17.3/20.4 | 1 | 1.4 | 11 | 5.9 | 1.31 | 2 | 2 | 4.5 | 2.7 | 0.77 | 0.40/0.52
Insulation Class |  | F | F | F | F | F | F | F | F | F | F | F | F | F | F | F
Temp Rise (ºC) |  | B | B | B | B | B | B | B | B | B | B | B | B | B | B | B
Bearings (DE) |  |  | 6206 ZZ C3 |  |  | 6004-2RS | 6205-2RS |  | NJ 312E C4
Bearings (NDE) |  |  | 6307 ZZ C3 |  |  | 6004-2RS | 6205-2RS |  | 6204ZZ C3
Duty |  | S4 | S4 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1 | S1
Remarks |  | Extended shaft for brake mounting, BRAKE DETAILS: HUB BORE DIA : 28MM, WATT : 50W, COIL OPTG.VOLG.- 190 VDC, TORQUE : 60NM, BRAKE TYPE: 14.458, SIZE 14, EMCO SIMPLATROLL D.C.SPRING APPLIED BRAKE | DUAL SPEED MOTOR SHAFT: EXTENDED SHAFT FOR BRAKE MOUNTING BRAKE DETAILS: HUB BORE DIA : 11MM WATT : 20W COIL OPTG.VOLG.- 190 VDC TORQUE : 10NM BRAKE TYPE: 14.458, EMCO SIMPLATROLL D.C.SPRING APPLIED BRAKE |  | DUAL SPEED MOTOR | Bearings should be Deep groove ball bearing with seals | Bearings should be Deep groove ball bearing with seals |  | EXTENDED SHAFT ON BOTH SIDE | 8 Pole 3 Phase motor runs on Single phase supply, Indoor AC blower motor for Bluestar 5.5 TR Tower AC | MOTOR, OUTDOOR, TOWER A.C., 1PHASE, 250W Make: Lawkim Ltd Customer Part No: M S0106-00000 1/3 HP 250W 920RPM FR B48 230V AC 1PH 50Hz Amb 40°C 2A CL B INSCAP 10μF 440V AC ROT CWSE Thermally Protected Permanently lubricated Lawkim Ref Model No: LK4111 | AC Blower motor, 750 Watt, 1 HP, 230 V AC, 920 RPM, FR B48, Rotation - CCWLE, Capacitor - 20 MFD 440 VAC, Model No. - LK4109 | AC Blower motor, 370 Watt, 1/2 HP, 230 V AC, 920 RPM, FR B48, Rotation - CWLE, Capacitor - 10 MFD 440 VAC, Model No. - LK4110 | AC Oudoor Unit Motor, Single Phase, 370 Watts, 940 RPm, 2.7 Amps, Capacitor - 12.5 Micro farad, Type - 2HS1 090-0503-A00002 |  | Capacitor - 8 Micro farad 3 Phase motor runs on Single phase supply

## Sheet2
ILMS & PA Fan LOP | 5.5 | 132S & ND132S | 1456 & 1430 | Foot Mounted & Vertical Flange Mounted
Roof Exhaust | 5.5 |  | 960
SAC Blower Motor & impellar agitator motor | 3.7 | 112 &112M | 1430 | B5
2.2 KW Motor |  | Frame size and Mounting different
Clinker Grinder, STP Blower & Sludge Blower | 7.5 KW | Same Motor